## Sheet1
Tr | 50% | Wells | Kuwait
KOC
Tr | 25%
Oil & gas | Upsteram
Swtichgear | 5M USD | 8USD
cables
Busbar
Future Margin
ask question to client
do you have any upgradation plan?
if you have plan, how many phases or within how many years ?

## Sheet2
Request for Information
site server y
1 | what is the source of supply ?
2 | nearst substation available ?
3 | how many source of incomer needed?
4 | what is existing votlage level adopted in the plan?
5 | what is the existing plant pihlopsohy follwoed ?

## Sheet3
design
| Service | Type | Shaft power | C/E | Rated Power | Demand factor | Efficiency @ Demand | Power Factor @ Demand | Duty | Continuous (F) |  | Intermittent G) |  | Standby or Spare (H) |  |  | Absorbed kW * TAN (COS-1 (Power Factor at Demand))
|  |  | kW | [6 empty] | kW | kVAr | kW | kVAr | kW | kVAr
Case 1 | Motor for Thruster A | Motor | 25 | E | 30 | 0.83333 | 0.955 | 0.89 | C | 26.178 | 13.4114
Case 1 | Motor for Thruster B | Motor | 25 | E | 30 | 0.83333 | 0.955 | 0.89 | S |  |  |  |  | 26.178 | 13.4114
cASe 2 | Motor for Compressor | Motor | 115 | E | 160 | 0.71875 | 0.955 | 0.89 | C | 120.4188 | 61.6924
Case 3 | Area Lighting | non motor | 100 | C | 100 | 1 | 1 | 0.95 | C | 100 | 32.8684
Caae 4 | Heater for VR tank | non motor | 95 | E | 118.75 | 0.8 | 0.89 | 0.95 | C | 106.7416 | 35.0843
[10 empty] | 353.3384 | 143.0565 | 0 | 0 | 26.178 | 13.4114
[7 empty] | X | Y | Z | [7 empty] | Any motor
[7 empty] | 1 | 0.5 | 0.1
[5 empty] | Maximum normal running plant load (Demand load) = x(%)F + y(%)G |  |  |  |  | 353.3384 | Kw
[10 empty] | 143.0565 | KVAR
[10 empty] | 381.1997 | Kva | [6 empty] | 0-24 | hrs
|  |  | Peak load = x(%)F + y(%)G + z(%)H | [6 empty] | 355.9562 | Kw
[10 empty] | 144.3976 | KVAR | [6 empty] | 2PMto 2.30pm | 0.5 | Hrs
[10 empty] | 384.1295 | Kva |  | 554.4595 | A
VFD
[13 empty] | 630 | A |  |  |  | SOFT STARTER
|  |  |  | 2W+1S | [13 empty] | SRAR DELTA
1W+1S
Continuous
|  |  | Intermittent | [11 empty] | 9 | 80 | W |  | 720 | W
|  |  | Standby | [20 empty] | E |  | 150 | LUX | FOR PROCESS AREA
[24 empty] | A |  | 25600 |  | for EL 100 | M | grid | A-H,1-16
[15 empty] | 3 | 80 | W |  | 240 | W |  |  |  | F |  | 4500 | Lumen |  | 100 | W
[24 empty] | UF |  | 1
[15 empty] | 5 | 80 | W |  | 400 | W |  |  |  | MF |  | 0.7
[15 empty] | 7 | 80 | W |  | 560 | W | 7 to 9 |  |  | N |  | 1219.0476
[24 empty] | W |  | 100
[24 empty] | POWER |  | 121.9048 | kW
[16 empty] | Sanctioned |  |  | 720 |  | W
|  |  | 1 | [15 empty] | 0.77778
|  |  |  | A | [11 empty] | EB |  | SLAB | FIXED COST |  | 720 | 2 | = | 1440 | INR
[16 empty] | EB |  | SLAB | VARIABLE COST |  | 720 | 6 | = | 4320 | INR