## Annexure A
PROJECT TITLE : | [13 empty] | CONTRACT No. : |  |  |  |  | DOCUMENT No. : | [6 empty] | Rev.00
DOCUMENT TITLE : | [18 empty] | DATE : |  |  |  | 19.09.2022
Annexure-A Project Load List-SS-01
Sl. No. | EQUIPMENT DETAILS | [6 empty] | ABSORBED LOAD |  | EQUIPMENT RATING |  | LOAD FACTOR C = A / B |  | EFFICIENCY @ LOAD FACTOR - C |  | COSθ (P.F.) @ LOAD FACTOR - C | CONSUMED LOAD | [8 empty] | REMARKS | FED FROM
| EQUIPMENT DESCRIPTION |  | EQUIPMENT TAG NO |  |  |  | DUTY | [9 empty] | kW = A/D |  |  |  | kVAR = kW x TANθ
[6 empty] | VOLTAGE | [10 empty] | CONTINUOUS |  |  | INTERMITTENT |  |  | STAND-BY
[9 empty] | A |  | B |  | C |  | D |  |  |  | E |  |  | F |  |  | G
[6 empty] | kV | C / I / S | kW |  | kW |  | Decimals |  | % |  | Decimals | kW | kVAR |  | kW | kVAR |  | kW | kVAR
1 | OIL DESALTING FEED PUMP A (TRAIN1) |  | 112101PA001A |  |  | 0.4 | C | 112 |  | 160 |  | 0.7 |  | 95 |  | 0.85 | 117.8947 | 73.0646 |  | - | - |  | - | -
2 | OIL DESALTING FEED PUMP B (TRAIN1) |  | 112101PA001B |  |  | 0.4 | S | 112 |  | 160 |  | 0.7 |  | 95 |  | 0.85 | - | - |  | - | - |  | 117.8947 | 73.0646
3 | OIL DESALTING FEED PUMP A (TRAIN2) |  | 112102PA001A |  |  | 0.4 | C | 112 |  | 160 |  | 0.7 |  | 95 |  | 0.85 | 117.8947 | 73.0646 |  | - | - |  | - | -
4 | OIL DESALTING FEED PUMP B (TRAIN2) |  | 112102PA001B |  |  | 0.4 | S | 112 |  | 160 |  | 0.7 |  | 95 |  | 0.85 | - | - |  | - | - |  | 117.8947 | 73.0646
5 | RECYCLE WATER PUMP A (TRAIN1) |  | 112101PA002A |  |  | 0.4 | C | 10.5 |  | 15 |  | 0.7 |  | 95 |  | 0.85 | 11.0526 | 6.8498 |  | - | - |  | - | -
6 | RECYCLE WATER PUMP B (TRAIN1) |  | 112101PA002B |  |  | 0.4 | S | 10.5 |  | 15 |  | 0.7 |  | 95 |  | 0.85 | - | - |  | - | - |  | 11.0526 | 6.8498
7 | RECYCLE WATER PUMP A (TRAIN2) |  | 112102PA002A |  |  | 0.4 | C | 10.5 |  | 15 |  | 0.7 |  | 95 |  | 0.85 | 11.0526 | 6.8498 |  | - | - |  | - | -
8 | RECYCLE WATER PUMP B (TRAIN2) |  | 112102PA002B |  |  | 0.4 | S | 10.5 |  | 15 |  | 0.7 |  | 95 |  | 0.85 | - | - |  | - | - |  | 11.0526 | 6.8498
9 | POWER TRANSFORMER (DEHYDRATOR) (TRAIN1) |  | 112101ET001 |  |  | 0.4 | C | 56 |  | 80 |  | 0.7 |  | 95 |  | 0.85 | 58.9474 | 36.5323 |  | - | - |  | - | -
10 | POWER TRANSFORMER (DESALTER) (TRAIN 1) |  | 112101ET002 |  |  | 0.4 | C | 56 |  | 80 |  | 0.7 |  | 95 |  | 0.85 | 58.9474 | 36.5323 |  | - | - |  | - | -
11 | POWER TRANSFORMER (DEHYDRATOR) (TRAIN2) |  | 112102ET001 |  |  | 0.4 | C | 56 |  | 80 |  | 0.7 |  | 95 |  | 0.85 | 58.9474 | 36.5323 |  | - | - |  | - | -
12 | POWER TRANSFORMER (DESALTER) (TRAIN 2) |  | 112102ET002 |  |  | 0.4 | C | 56 |  | 80 |  | 0.7 |  | 95 |  | 0.85 | 58.9474 | 36.5323 |  | - | - |  | - | -
13 | WASH WATER PUMPS |  | 105200PA002C |  |  | 0.4 | C | 25.9 |  | 37 |  | 0.7 |  | 95 |  | 0.85 | 27.2632 | 16.8962 |  | - | - |  | - | -
14 | WASH WATER PUMPS |  | 105200PA002D |  |  | 0.4 | C | 25.9 |  | 37 |  | 0.7 |  | 95 |  | 0.85 | 27.2632 | 16.8962 |  | - | - |  | - | -
15 | COMPRESSOR A |  | 104600KCOC1A |  |  | 0.4 | C | 112 |  | 160 |  | 0.7 |  | 95 |  | 0.85 | 117.8947 | 73.0646 |  | - | - |  | - | -
16 | POTABLE WATER PUMP |  | 105300PA001A |  |  | 0.4 | C | 5.25 |  | 7.5 |  | 0.7 |  | 95 |  | 0.85 | 5.5263 | 3.4249 |  | - | - |  | - | -
17 | POTABLE WATER PUMP |  | 105300PA001B |  |  | 0.4 | S | 5.25 |  | 7.5 |  | 0.7 |  | 95 |  | 0.85 | - | - |  | - | - |  | 5.5263 | 3.4249
Peak Load (or) Maximum Demand (A) = (100% . E + 30% . F + 00% . G) = | [13 empty] | TOTAL |  |  | 671.632 | 416.24 |  | 0 | 0 |  | 263.43 | 163.26 |  | Power Factor for Peak Load:
|  | 671.632 | kW; | 416.24 | kVAR; |  |  | 790.156 |  | kVA;
[17 empty] | 790.156 |  |  | 0 |  |  | 309.92 |  |  | 0.85
Total Load = |  | 671.632 | kW; | 416.24 | kVAR; |  |  | 790.156 | kVA;
Peak Load (or) Maximum Demand (A) |  |  |  | 790.156 | kVA;
NOTES: | [9 empty] | ABBREVIATIONS:
1. INDICATED LOADS ARE CONSIDERED FOR BACK UP SUPPLY BASED ON FIELD DATA. | [9 empty] | C - Continuos load
2. EFFICIENCY AND POWER FACTOR OF ALL EQUIPMENT'S ARE BASED ON REPUTED CATALOUGE | [9 empty] | S- Standby load
I-Intermitent Loads
Note on H23: Wisam Hussain Malik Alalwan: Pump is continuous

## Trafo sizing
DISTRIBUTION TRANSFORMER SIZING CALCULATION | [9 empty] | DISTRIBUTION TRANSFORMER SIZING CALCULATION
TOTAL OPERATING LOAD |  | : | 790.156 | KVA | AS PER ELECTRICAL LOAD DISTRIBUTION | [5 empty] | THE TOTAL LOAD IN KVA |  |  |  |  | 971.8919 | KVA
20 % OF MARGIN |  | : | 158.0312 | KVA | [6 empty] | THE TRANSFORMER SELECTED |  |  |  |  | 2000 | KVA
3 % OF LOSSES |  | : | 23.7047 | KVA
TOTAL LOAD |  | : | 971.8919 | KVA | [6 empty] | CALCULATION OF OVERLOAD CAPACITY OF TRANSFORMER AS PER IEC 60076/ IS-6600 AS PER CL 5.1 ON PAGE NO 6 | [7 empty] | 0
CONSIDERING THE P.F. |  | COS F | = | 0.85 | AVERAGE PF TAKEN FROM LOAD LIST | [5 empty] | K1 |  | INITIAL LOAD AS A FRACTION OF RATED KVA
SO, |  | SIN F | = | 0.52678 | [6 empty] | K2 |  | PERMISSIBLE LOAD AS A FRACTION OF RATED KVA (MAY BE GREATER THAN UNITY)
[11 empty] | h |  | DURATION OF K2 IN HOURS (CONSIDERING FOR 2 HOURS)
HENCE, |  | KVA | = |  |  | 971.8919 | KVA |  |  |  | θa |  | TEMPERATURE OF COOLING MEDIUM (WEIGHTED AVERAGE) (35 °C FOR THIS CASE) | [5 empty] | S=P+iQ
[11 empty] | NOTE | K1 | = | S1 | AND | K2 | = | S2
TOTAL LOAD IN KVA AT 0.85 P.F. LAG |  |  | = | (KVA X COS F) + j (KVA X SIN F) | [9 empty] | Sr |  |  |  | Sr
|  |  | = | 826.1081 | + j | 511.9758 | KVA |  | ………….[1]
[11 empty] | S1 |  | IS ANY VALUE OF POWER |  |  | = | 971.8919 | KVA
THE HIGHTEST MOTOR LOAD |  |  | = | 160 | KW | Refer Note 1 |  |  |  |  | Sr |  | IS RATED KVA |  |  | = | 2000 | KVA
FULL LOAD CURRENT OF 160 KW MOTOR |  |  | = | 286.0023 | AMP | [5 empty] | K1 |  |  |  |  | = | 0.48595 | KVA
THE P.F. OF | 160 | KW MOTOR | = | 0.85 | (i.e. COS F)
HENCE, SIN F |  |  | = | 0.52678
SO, THE MOTOR KVA RATING |  |  | = | 198.1424 | KVA | [5 empty] | CONSIDER OVERLOAD CAPACITY FOR 2 HOUR WHICH IS MUCH HIGHER THAN THE STARTING TIME OF HIGHEST RATED
MOTOR (APPROX. 10-12 SEC. MAX)
TOTAL MOTOR LOAD IN KVA AT 0.85 P.F. LAG |  |  | = | (KVA X COS F) + j (KVA X SIN F)
|  |  | = | 168.4211 | + j | 104.378 | KVA |  | ………….[2] |  | THEREFORE | h | = | 2 | HOUR
SUBTRACTING [2] FROM [1] |  |  | = | 657.687 | + j | 407.5978 | KVA |  | ………….[3] |  | CONSIDER THE WEIGHTED AVERAGE ANNUAL AMBIENT TEMPERATURE OF COOLING MEDIUM AS 35 °C
STARTING METHOD OF THE MOTOR [I st.] |  |  | = | DOL | [6 empty] | THEREFORE | θa | = | 35 | °C
SO THE STARTING CURRENT OF MOTOR |  |  | = | 1716.014 | AMP | NOTE NO. 1 (FOR DOL Ist=6*Ifl)
STARTING P.F. OF MOTOR CONSIDERED AS |  |  | = | 0.2 | (i.e. COS F)
HENCE, SIN F |  |  | = | 0.9798 | [6 empty] | FROM THE REFERENCE OF TABLE NO. 6 OF IS-6600 FOR PERMISSIBLE VALUE OF K2 AT θa = 32 °C IS TAKEN AS:
[11 empty] | K2 | = | 1.29
STARTING CURRENT AT 0.2 P.F. |  |  | = | (I st. X COS F) + j (I st. X SIN F)
|  |  | = | 343.2028 | + j | 1681.3435 |  | AMP |  | HENCE, | S2 | = | K2 X Sr | = | 2042.07 | KVA
STARTING KVA AT 0.2 P.F. |  |  | = | 1.732 X 0.400 (I st. X COS F) + j (I st. X SIN F)
|  |  | = | 237.7709 | + j | 1164.8348 |  | KVA | ………….[4] | THE TRANSFORMER IS CAPABLE FOR THE OVERLOAD CAPACITY OF |  |  |  |  | 102.1035 | % |  |  |  | 1188.8545
FROM ABOVE IT IS CONCLUDED THAT SINCE S2 IS GREATER THAN KVA DEMAND DURING STARTING OF HIGHEST RATED HENCE MOTOR,
ADDING [3] AND [4] |  |  | = | 895.4579 | + j | 1572.4326 | KVA |  | ………….[5] | SELECTED KVA RATING OF THE TRANSFORMER (2000 KVA) IS CORRECT.
|  |  | = | 1809.5273 |  |  | KVA |  | ………….[6]
NOTES :
1] THE STARTING CURRENT IS CONSIDERED AS 6 TIMES THE MOTOR FULL LOAD CURRENT,
IT IS ASSUMED THE MOTOR INITIALLY STARTS AT 60KW THEN TRANSFERRED TO 90KW WITH CLOSE/OPEN TRANSITION
2) SELECTED TRANSFORMER SHALL BE 1500kVA ONAN TO SUIT THE EXISTING SYSTEM.
THE TRANSFORMER RATING CONSIDERED AS |  |  |  | = | 2000 | KVA
NOW, AS PER THE FORMULA
|  | KVA RATING OF TRANSFORMER | = | 1.732 X VOLTAGE X CURRENT
| 2000 | = | 1.732 | X | 400 | X | CURRENT | (TRAFO. RATING WITH ONAN COOLING)
| SO, | CURRENT | = | 2886.836 | AMP
| THE INCOMER RATING AS PER DESIGN |  | = | 3200 | AMP
CONSIDERING THE DERATING & LIFE TIME OF BREAKER, THE INCOMER RATING OF 3200 AMP IS RECOMMENDED

## Short time overloading check
Short time overloading check
Starting requirement of Largest Motor
Here Largest motor is high capacity LP Flare motor |  | = | 160 | kW
Voltage |  | = | 400 | V
Running power factor of the motor | Cos Φ r | = | 0.85
Starting power factor of the motor | Cos Φs | = | 0.2
Efficiency of the motor |  | = | 0.95
Largest motor starting current |  | = | 6 times the full load current
Full load current of motor | Ir | = | (Motor rating in kW) / (1.732*Vs * η * cos Φ)
|  | = | 286.0023
| Ir | = | (Motor rating in kW) / (1.732*Vs * η * cos Φ)
Motor power during at full load |  | = | 198.1424 | kVA
Starting current of largest motor | IS | = | 6 * Ir
|  | = | 1716.014
Starting kW of largest motor | M (SKW) | = | 1.732*VS * IS * cos Φ
|  | = | 237.7709
Starting kVA of largest motor | M (SKVA) | = | M (SKW) / Cos Φs
|  | = | 1251.4258 | kVA
Total KVA Required |  | = | BASE LOAD + STARTING LOAD OF MOTOR
Base load on DG |  | = | Total Load connected ( Except largest motor rating )
|  | = | 713.3756 | kVA
Total kVA Required during starting of Largest motor |  | = | Base Load+ M (SKVA)
|  | = | 1964.8014 | kVA
DG Size selected |  | = | 2040 | kVA
As per IEC–60034(Part-1), Clause no. 9.3.2, AC Generators shall be capable of withstanding a current equal to 1.5 times the Rated current for not less than 30 sec under over loading condition
Hence D.G, under over loading |  | = | 2040*1.5
|  | = | 3060 | kVA
| 3060 | > | 1964.8014 | kVA
HENCE, 2040 kVA GENERATOR IS ADEQUATE